## Version infor.
Description | status | Function code | address-decimal(10) | address-decimal(16)
| Read-only integer quantity | 0X04 | 256 | 100
| Read-only integer quantity | 0X04 | 512 | 200
| Read-only integer quantity | 0X04 | 4000 | FA0

## User operation command
说明 | Description | 状态 | status | Function code | Site name | address-decimal(10) | address-decimal(16)
0XFF00：开机 | 0XFF00： ON | 只写开关量 | Write only the on-off quantity | 0X05 | Unit on | 0 | 0
0XFF00：关机 | 0XFF00：OFF |  |  |  | Unit off | 1 | 1
0XFF00：复位 | 0XFF00：Reset |  |  |  | Reset command | 8 | 8
强制除霜 0XFF00：有效 | Force Defrost 0XFF00：valid |  |  |  | 00#module defrosting demand | 16 | 10
[5 empty] | 01#module defrosting demand | 17 | 11
[5 empty] | 02#module defrosting demand | 18 | 12
[5 empty] | 03#module defrosting demand | 19 | 13
[5 empty] | 04#module defrosting demand | 20 | 14
[5 empty] | 05#module defrosting demand | 21 | 15
[5 empty] | 06#module defrosting demand | 22 | 16
[5 empty] | 07#module defrosting demand | 23 | 17
初始化命令 0XFF00：有效 | Initialization command 0XFF00：valid |  |  |  | Spare | 128 | 80
[5 empty] | Factory parameters initialization | 129 | 81
[5 empty] | Inverter initialization | 130 | 82
[5 empty] | System maintenance initialization | 131 | 83
[5 empty] | Spare | 132 | 84
[5 empty] | Spare | 133 | 85
[5 empty] | Spare | 134 | 86
[5 empty] | Spare | 135 | 87
[5 empty] | Initialization of compressor running time | 136 | 88
[5 empty] | Initialization of compressor running time | 137 | 89
集中命令 0XFF00：有效 | Centralized command 0XFF00：valid |  |  |  | A zone on | 1024 | 400
[5 empty] | A zone off | 1025 | 401
[5 empty] | B zone on | 1026 | 402
[5 empty] | B zone off | 1027 | 403
[5 empty] | Domestic hot water on | 1028 | 404
[5 empty] | Domestic hot water off | 1029 | 405
[5 empty] | Domestic hot water pump timer on | 1030 | 406
[5 empty] | Domestic hot water pump timer off | 1031 | 407
[5 empty] | Forced domestic hot water on | 1032 | 408
[5 empty] | Forced domestic hot water off | 1033 | 409
[5 empty] | Disinfection timer on | 1034 | 40A
[5 empty] | Disinfection timer off | 1035 | 40B
[5 empty] | Domestic hot water pump for disinfection on | 1036 | 40C
[5 empty] | Domestic hot water pump for disinfection off | 1037 | 40D
[5 empty] | Holiday Away on | 1038 | 40E
[5 empty] | Holiday Away off | 1039 | 40F
[5 empty] | Holiday Home on | 1040 | 410
[5 empty] | Holiday Home off | 1041 | 411
[5 empty] | Force open T heat on | 1042 | 412
[5 empty] | Force open T heat on | 1043 | 413
[5 empty] | Force open I heat on | 1044 | 414
[5 empty] | Force open I heat off | 1045 | 415
[5 empty] | Force AHS on | 1046 | 416
[5 empty] | Force AHS off | 1047 | 417
[5 empty] | Spare | 1048 | 418
[5 empty] | Spare | 1049 | 419
[5 empty] | Spare | 1050 | 41A
[5 empty] | Floor preheat on | 1051 | 41B
[5 empty] | Floor preheat off | 1052 | 41C
[5 empty] | Floor dry up on | 1053 | 41D
[5 empty] | Floor dry up off | 1054 | 41E
[5 empty] | System empty on | 1055 | 41F
[5 empty] | System empty off | 1056 | 420
[5 empty] | Pump test on | 1057 | 421
[5 empty] | Pump test off | 1058 | 422
[5 empty] | Cool test on | 1059 | 423
[5 empty] | Cool test off | 1060 | 424
[5 empty] | Heat test on | 1061 | 425
[5 empty] | Heat test off | 1062 | 426
[5 empty] | Spare | 1063 | 427
[5 empty] | Spare | 1064 | 428
[5 empty] | Hotwater test on | 1065 | 429
[5 empty] | Hotwater test on | 1066 | 42A
[5 empty] | Spare | 1067 | 42B
[5 empty] | Spare | 1068 | 42C
[5 empty] | Ability test on | 1069 | 42D
[5 empty] | Ability test off | 1070 | 42E
[5 empty] | Recycle refrig. on | 1071 | 42F
[5 empty] | Recycle refrig. off | 1072 | 430
[5 empty] | Quiet_mode on | 1073 | 431
[5 empty] | Quiet_mode off | 1074 | 432
[5 empty] | LEVEL.I | 1075 | 433
[5 empty] | LEVEL.II | 1076 | 434
[5 empty] | HOLIDAY_AWAY_ThS on | 1077 | 435
[5 empty] | HOLIDAY_AWAY_ThS off | 1078 | 436
[5 empty] | HOLIDAY_AWAY_ThwS on | 1079 | 437
[5 empty] | HOLIDAY_AWAY_ThwS off | 1080 | 438
[5 empty] | Mnl test on | 1081 | 439
[5 empty] | Mnl test off | 1082 | 43A
手动调试 0XFF00：置位 0X0000：清零 | Manual debugging 0XFF00：setting 0X0000：reset |  |  |  | Desrost | 2048 | 800
[5 empty] | Error | 2049 | 801
[5 empty] | AHS | 2050 | 802
[5 empty] | S3V1 valve state | 2051 | 803
[5 empty] | S3V3 valve state | 2052 | 804
[5 empty] | S3V2 valve state | 2053 | 805
[5 empty] | Anti-freezing electric heater | 2054 | 806
[5 empty] | PUMPret | 2055 | 807
[5 empty] | PUMPsl | 2056 | 808
[5 empty] | PUMPm | 2057 | 809
[5 empty] | TBH | 2058 | 80A
[5 empty] | IBH1 | 2059 | 80B
[5 empty] | IBH2 | 2060 | 80C
[5 empty] | PUMPo | 2061 | 80D
[5 empty] | PUMPf | 2062 | 80E
[5 empty] | QZH1 | 2063 | 80F
[5 empty] | QZH2 | 2064 | 810
[5 empty] | DPH | 2065 | 811
[5 empty] | RV | 2066 | 812
[5 empty] | EXVli | 2067 | 813

## Machine infor.
Site name | address-decimal(10) | address-decimal(16) | Description | State | Unit status
Unit status | 768 | 300 | B0: The unit is in standby state B1: The unit is starting B2: The unit is running B3: The unit is shutting down B4: The unit is in serious alarm state B5: B6: B7: B8: The unit is warming up B9: The unit is faulty B10: The unit is antifreezing B11: The unit is defrosting B12: B13: B14: B15: | read-only integer | 0X04
Compressor number of 0#module | 769 | 301
mode of air conditioner | 770 | 302
current running mode | 771 | 303 | 0: None; 1: Cooling; 2: Heating; 3: Auto; 4: Hot water;
Target temperature for adjustion | 772 | 304 | Unit 0.1℃
Control temperature for adjustion | 773 | 305 | Unit 0.1℃
Module | 791 | 317 | B0:0#Module use/unuse B1:1#Module use/unuse B2:2#Module use/unuse B3:3#Module use/unuse B4:4#Module use/unuse B5:5#Module use/unuse B6 6#Module use/unuse B7:7#Module use/unuse B8: B9: B10: B11: B12: B13: B14: B15:
Module number | 792 | 318
Operating status | 793 | 319 | 0: The unit is in standby state 1: The unit is starting 2: The unit is running 3: The unit is shutting down 4: The unit is in serious alarm state
Upper limit temperature of zone A | 794 | 31A
Lower limit temperature of zone A | 795 | 31B
Upper limit temperature of zone B | 796 | 31C
Lower limit temperature of zone B | 797 | 31D
DHW upper limit temperature | 798 | 31E
DHW lower limit temperature | 799 | 31F
Upper limit temperature of cooling | 800 | 320
Lower limit temperature of cooling | 801 | 321
Upper limit temperature of heating | 802 | 322
Lower limit temperature of heating | 803 | 323
Upper limit temperature of cooling | 804 | 324
Lower limit temperature of heating | 805 | 325
Upper limit temperature of cooling | 806 | 326
Lower limit temperature of heating | 807 | 327
Test run | 910 | 38E | B0: System emptying test run B1: Water pump test run B2: Cooling test run B3: Heating test run B4: Hot water test run
run flag 0 | 912 | 390 | B0: Zone A operation sign B1: Zone B operation sign B2: Hot water operation sign B3: Timing dometic hot water pump operation sign B4: Forced hot water mode function operation sign B5: Timing disinfection function operation sign B6: Domestic hot water pump disinfection operation Sign B7: holiday away mode operation sign B8: holiday home mode operation sign B9: forced water tank electric heating operation sign B10: forced auxiliary electric heating operation sign B11: external heat source operation sign B12: floor heating preheating function operation sign B13: floor heating Drying function running sign B14: ability test running sign B15: fluorine collection running sign
run flag 1 | 913 | 391 | B0: silent mode sign B1: silent mode level: 0: level one; 1: level two
Compressor number of 0#module | 1000 | 3E8
Compressor number of 1#module | 1001 | 3E9
Compressor number of 2#module | 1002 | 3EA
Compressor number of 3#module | 1003 | 3EB
Compressor number of 4#module | 1004 | 3EC
Compressor number of 5#module | 1005 | 3ED
Compressor number of 6#module | 1006 | 3EE
Compressor number of 7#module | 1007 | 3EF
Running time of the system | 1024 | 400 | Unit: hour
Compressor running time 1 | 1025 | 401
Compressor running time 2 | 1026 | 402
Compressor running time 3 | 1027 | 403
Compressor running time 4 | 1028 | 404
Compressor running time 5 | 1029 | 405
Compressor running time 6 | 1030 | 406
Compressor running time 7 | 1031 | 407
Compressor running time 8 | 1032 | 408
Inverter status | 1033 | 409 | Bit 0: ready for power-on Bit 1: ready for operation bit 2: running bit 3: Error Bit 4: OFF3 stop valid (0 is valid) bit 5: OFF3 stopping Bit 6: Charging contactor disconnected bit 7: Alarm (non-stop alarm) Bit 8: Spare Bit 9: Spare Bit 10:Spare Bit 11:Spare Bit 12:Spare Bit 13:Spare Bit 14:Forward running Bit 15:Spare
Running speed of compressor | 1034 | 40A | unit 0.1rps
module temperature | 1035 | 40B | unit 0.1℃
Output Power | 1036 | 40C | unit 0.1kW
Given speed | 1037 | 40D | unit 0.1rps
Output current | 1038 | 40E | unit 0.1A
output torque | 1039 | 40F | unit 0.1%
output voltage | 1040 | 410 | unit 0.1V
bus voltage | 1041 | 411 | unit 0.1V
error code | 1042 | 412 | value of 0 means there is no fault, otherwise it means the current fault code, see "Inverter Faults" in the manufacturer's manual for details
inverter input current | 1043 | 413 | Unit 0.1A
PFC temperature | 1044 | 414 | Unit 0.1℃
current compressor speed | 1045 | 415 | Unit 0.1rps
Frequency limit information | 1046 | 416 | See "Inverter frequency limit information" in the manufacturer's manual
spare | 1047 | 417
spare | 1048 | 418

## Analog
Explanation: -32700(0x8044) indicates that the probe does not exist, -32701(0x8043) indicates that the probe is faulty, -32702(0x8042) indicates that the probe is disconnected, -32703(0x8041) indicates that the probe is short-circuited
The module resources |  | address-decimal(10) | [7 empty] | address-decimal(16) | [7 empty] | system resource |  | address-decimal(10) | address-decimal(16)
site name | Unit | 0#module | 1#module | 2#module | 3#module | 4#module | 5#module | 6#module | 7#module | 0#module | 1#module | 2#module | 3#module | 4#module | 5#module | 6#module | 7#module | site name | unit
|  | 1300 | 1556 | 1812 | 2068 | 2324 | 2580 | 2836 | 3092 | 514 | 614 | 714 | 814 | 914 | A14 | B14 | C14 | Indoor Tenperature | 0.1℃ | 3348 | D14
Main circuit electronic expansion valve opening | Step | 1301 | 1557 | 1813 | 2069 | 2325 | 2581 | 2837 | 3093 | 515 | 615 | 715 | 815 | 915 | A15 | B15 | C15 | \ |  | 3349 | D15
Auxiliary circuit electronic expansion valve opening | Step | 1302 | 1558 | 1814 | 2070 | 2326 | 2582 | 2838 | 3094 | 516 | 616 | 716 | 816 | 916 | A16 | B16 | C16 | Ambient Temperature | 0.1℃ | 3350 | D16
Fin temperature | 0.1℃ | 1303 | 1559 | 1815 | 2071 | 2327 | 2583 | 2839 | 3095 | 517 | 617 | 717 | 817 | 917 | A17 | B17 | C17 | hot water tank temperature | 0.1℃ | 3351 | D17
Discharge temperature | 0.1℃ | 1304 | 1560 | 1816 | 2072 | 2328 | 2584 | 2840 | 3096 | 518 | 618 | 718 | 818 | 918 | A18 | B18 | C18 |  | 0.1℃ | 3352 | D18
Sunciotn Temperature | 0.1℃ | 1305 | 1561 | 1817 | 2073 | 2329 | 2585 | 2841 | 3097 | 519 | 619 | 719 | 819 | 919 | A19 | B19 | C19 | System total outlet water temperature | 0.1℃ | 3353 | D19
|  | 1306 | 1562 | 1818 | 2074 | 2330 | 2586 | 2842 | 3098 | 51A | 61A | 71A | 81A | 91A | A1A | B1A | C1A | solar temperature | 0.1℃ | 3354 | D1A
|  | 1307 | 1563 | 1819 | 2075 | 2331 | 2587 | 2843 | 3099 | 51B | 61B | 71B | 81B | 91B | A1B | B1B | C1B | Buffer water tank upper temperature | 0.1℃ | 3355 | D1B
Evaporating temperature | 0.1℃ | 1308 | 1564 | 1820 | 2076 | 2332 | 2588 | 2844 | 3100 | 51C | 61C | 71C | 81C | 91C | A1C | B1C | C1C | Buffer water tank lower temperature | 0.1℃ | 3356 | D1C
Condensing temperature | 0.1℃ | 1309 | 1565 | 1821 | 2077 | 2333 | 2589 | 2845 | 3101 | 51D | 61D | 71D | 81D | 91D | A1D | B1D | C1D |  | 0.1℃ | 3357 | D1D
Evaporating prssure | 0.1℃ | 1310 | 1566 | 1822 | 2078 | 2334 | 2590 | 2846 | 3102 | 51E | 61E | 71E | 81E | 91E | A1E | B1E | C1E |  |  | 3358 | D1E
condensing pressure | 0.1℃ | 1311 | 1567 | 1823 | 2079 | 2335 | 2591 | 2847 | 3103 | 51F | 61F | 71F | 81F | 91F | A1F | B1F | C1F |  |  | 3359 | D1F
Main valve target superheat | 0.1℃ | 1312 | 1568 | 1824 | 2080 | 2336 | 2592 | 2848 | 3104 | 520 | 620 | 720 | 820 | 920 | A20 | B20 | C20 |  |  | 3360 | D20
Main valve is currently overheated | 0.1℃ | 1313 | 1569 | 1825 | 2081 | 2337 | 2593 | 2849 | 3105 | 521 | 621 | 721 | 821 | 921 | A21 | B21 | C21 |  |  | 3361 | D21
Auxiliary valve target overheating | 0.1℃ | 1314 | 1570 | 1826 | 2082 | 2338 | 2594 | 2850 | 3106 | 522 | 622 | 722 | 822 | 922 | A22 | B22 | C22 | Underfloor heating water temperature | 0.1℃ | 3362 | D22
Auxiliary valve is currently overheated | 0.1℃ | 1315 | 1571 | 1827 | 2083 | 2339 | 2595 | 2851 | 3107 | 523 | 623 | 723 | 823 | 923 | A23 | B23 | C23 | 3 way valve 1 state |  | 3363 | D23
|  | 1316 | 1572 | 1828 | 2084 | 2340 | 2596 | 2852 | 3108 | 524 | 624 | 724 | 824 | 924 | A24 | B24 | C24 | 3 way valve 2 state |  | 3364 | D24
|  | 1317 | 1573 | 1829 | 2085 | 2341 | 2597 | 2853 | 3109 | 525 | 625 | 725 | 825 | 925 | A25 | B25 | C25 | 3 way valve 3 state |  | 3365 | D25
Difference between ambient temperature and fin temperature in frost-free operation | 0.1℃ | 1318 | 1574 | 1830 | 2086 | 2342 | 2598 | 2854 | 3110 | 526 | 626 | 726 | 826 | 926 | A26 | B26 | C26 |  |  | 3366 | D26
Frequency conversion target speed | 0.1rps | 1319 | 1575 | 1831 | 2087 | 2343 | 2599 | 2855 | 3111 | 527 | 627 | 727 | 827 | 927 | A27 | B27 | C27 |  |  | 3367 | D27
Frequency conversion current speed | 0.1rps | 1320 | 1576 | 1832 | 2088 | 2344 | 2600 | 2856 | 3112 | 528 | 628 | 728 | 828 | 928 | A28 | B28 | C28 |  |  | 3368 | D28
Inverter output voltage | 0.1V | 1321 | 1577 | 1833 | 2089 | 2345 | 2601 | 2857 | 3113 | 529 | 629 | 729 | 829 | 929 | A29 | B29 | C29 |  |  | 3369 | D29
Variable frequency output current | 0.1A | 1322 | 1578 | 1834 | 2090 | 2346 | 2602 | 2858 | 3114 | 52A | 62A | 72A | 82A | 92A | A2A | B2A | C2A
Inverter module temperature | 0.1℃ | 1323 | 1579 | 1835 | 2091 | 2347 | 2603 | 2859 | 3115 | 52B | 62B | 72B | 82B | 92B | A2B | B2B | C2B
Frequency conversion limit information |  | 1324 | 1580 | 1836 | 2092 | 2348 | 2604 | 2860 | 3116 | 52C | 62C | 72C | 82C | 92C | A2C | B2C | C2C
Variable frequency input current | 0.1A | 1325 | 1581 | 1837 | 2093 | 2349 | 2605 | 2861 | 3117 | 52D | 62D | 72D | 82D | 92D | A2D | B2D | C2D
Frequency conversion output power | 0.01 | 1326 | 1582 | 1838 | 2094 | 2350 | 2606 | 2862 | 3118 | 52E | 62E | 72E | 82E | 92E | A2E | B2E | C2E
Fan 1 target operation | rpm | 1327 | 1583 | 1839 | 2095 | 2351 | 2607 | 2863 | 3119 | 52F | 62F | 72F | 82F | 92F | A2F | B2F | C2F
Fan 1 current speed | rpm | 1328 | 1584 | 1840 | 2096 | 2352 | 2608 | 2864 | 3120 | 530 | 630 | 730 | 830 | 930 | A30 | B30 | C30
Fan 2 target operation | rpm | 1329 | 1585 | 1841 | 2097 | 2353 | 2609 | 2865 | 3121 | 531 | 631 | 731 | 831 | 931 | A31 | B31 | C31
Current speed of fan 2 | rpm | 1330 | 1586 | 1842 | 2098 | 2354 | 2610 | 2866 | 3122 | 532 | 632 | 732 | 832 | 932 | A32 | B32 | C32
\ |  | 1331 | 1587 | 1843 | 2099 | 2355 | 2611 | 2867 | 3123 | 533 | 633 | 733 | 833 | 933 | A33 | B33 | C33
\ |  | 1332 | 1588 | 1844 | 2100 | 2356 | 2612 | 2868 | 3124 | 534 | 634 | 734 | 834 | 934 | A34 | B34 | C34
Refrigerant gas side temperature | 0.1℃ | 1333 | 1589 | 1845 | 2101 | 2357 | 2613 | 2869 | 3125 | 535 | 635 | 735 | 835 | 935 | A35 | B35 | C35
Refrigerant liquid side temperature | 0.1℃ | 1334 | 1590 | 1846 | 2102 | 2358 | 2614 | 2870 | 3126 | 536 | 636 | 736 | 836 | 936 | A36 | B36 | C36
|  | 1335 | 1591 | 1847 | 2103 | 2359 | 2615 | 2871 | 3127 | 537 | 637 | 737 | 837 | 937 | A37 | B37 | C37
|  | 1336 | 1592 | 1848 | 2104 | 2360 | 2616 | 2872 | 3128 | 538 | 638 | 738 | 838 | 938 | A38 | B38 | C38
|  | 1337 | 1593 | 1849 | 2105 | 2361 | 2617 | 2873 | 3129 | 539 | 639 | 739 | 839 | 939 | A39 | B39 | C39
|  | 1338 | 1594 | 1850 | 2106 | 2362 | 2618 | 2874 | 3130 | 53A | 63A | 73A | 83A | 93A | A3A | B3A | C3A
|  | 1339 | 1595 | 1851 | 2107 | 2363 | 2619 | 2875 | 3131 | 53B | 63B | 73B | 83B | 93B | A3B | B3B | C3B
|  | 1340 | 1596 | 1852 | 2108 | 2364 | 2620 | 2876 | 3132 | 53C | 63C | 73C | 83C | 93C | A3C | B3C | C3C
|  | 1341 | 1597 | 1853 | 2109 | 2365 | 2621 | 2877 | 3133 | 53D | 63D | 73D | 83D | 93D | A3D | B3D | C3D
|  | 1342 | 1598 | 1854 | 2110 | 2366 | 2622 | 2878 | 3134 | 53E | 63E | 73E | 83E | 93E | A3E | B3E | C3E
|  | 1343 | 1599 | 1855 | 2111 | 2367 | 2623 | 2879 | 3135 | 53F | 63F | 73F | 83F | 93F | A3F | B3F | C3F
|  | 1344 | 1600 | 1856 | 2112 | 2368 | 2624 | 2880 | 3136 | 540 | 640 | 740 | 840 | 940 | A40 | B40 | C40
|  | 1345 | 1601 | 1857 | 2113 | 2369 | 2625 | 2881 | 3137 | 541 | 641 | 741 | 841 | 941 | A41 | B41 | C41
|  | 1346 | 1602 | 1858 | 2114 | 2370 | 2626 | 2882 | 3138 | 542 | 642 | 742 | 842 | 942 | A42 | B42 | C42
|  | 1347 | 1603 | 1859 | 2115 | 2371 | 2627 | 2883 | 3139 | 543 | 643 | 743 | 843 | 943 | A43 | B43 | C43
Plate heat exchanger inlet water temperature | 0.1℃ | 1348 | 1604 | 1860 | 2116 | 2372 | 2628 | 2884 | 3140 | 544 | 644 | 744 | 844 | 944 | A44 | B44 | C44
Plate heat exchanger outlet water temperature | 0.1℃ | 1349 | 1605 | 1861 | 2117 | 2373 | 2629 | 2885 | 3141 | 545 | 645 | 745 | 845 | 945 | A45 | B45 | C45
total water temperature | 0.1℃ | 1350 | 1606 | 1862 | 2118 | 2374 | 2630 | 2886 | 3142 | 546 | 646 | 746 | 846 | 946 | A46 | B46 | C46
ambient temperature | 0.1℃ | 1351 | 1607 | 1863 | 2119 | 2375 | 2631 | 2887 | 3143 | 547 | 647 | 747 | 847 | 947 | A47 | B47 | C47
Variable frequency water pump target speed | rpm | 1352 | 1608 | 1864 | 2120 | 2376 | 2632 | 2888 | 3144 | 548 | 648 | 748 | 848 | 948 | A48 | B48 | C48
The current flow of the variable frequency water pump | L/h | 1353 | 1609 | 1865 | 2121 | 2377 | 2633 | 2889 | 3145 | 549 | 649 | 749 | 849 | 949 | A49 | B49 | C49
Frequency conversion pump control signal | % | 1354 | 1610 | 1866 | 2122 | 2378 | 2634 | 2890 | 3146 | 54A | 64A | 74A | 84A | 94A | A4A | B4A | C4A
Frequency conversion pump feedback signal | % | 1355 | 1611 | 1867 | 2123 | 2379 | 2635 | 2891 | 3147 | 54B | 64B | 74B | 84B | 94B | A4B | B4B | C4B
Inverter water pump fault information |  | 1356 | 1612 | 1868 | 2124 | 2380 | 2636 | 2892 | 3148 | 54C | 64C | 74C | 84C | 94C | A4C | B4C | C4C
Unit calibration capability |  | 1357 | 1613 | 1869 | 2125 | 2381 | 2637 | 2893 | 3149 | 54D | 64D | 74D | 84D | 94D | A4D | B4D | C4D
The current capacity of the unit |  | 1358 | 1614 | 1870 | 2126 | 2382 | 2638 | 2894 | 3150 | 54E | 64E | 74E | 84E | 94E | A4E | B4E | C4E
256

## 04-Input, output
Read-only integer; function code: 04
point name | illustrate | Address (decimal) | [7 empty] | Address (hexadecimal) | [7 empty] | point name | illustrate | Address (decimal) | Address (hexadecimal)
|  | 0# module | 1# module | 2# module | 3# module | 4# module | 5# module | 6# module | 7# module | 0# module | 1# module | 2# module | 3# module | 4# module | 5# module | 6# module | 7# module
Press relay output | B0: frequency conversion compressor B1: four-way valve B2: liquid injection valve B3: B4: B5: crankshaft electric heating 1 B6: B7: crankshaft electric heating 2 | 1283 | 1539 | 1795 | 2051 | 2307 | 2563 | 2819 | 3075 | 503 | 603 | 703 | 803 | 903 | A03 | B03 | C03 | System relay output | B0: Defrost indication B1: Fault indication B2: External heat source B3: Electromagnetic three-way valve 1 B4: Electromagnetic three-way valve 3 B5: Electromagnetic three-way valve 2 B6: Water tank electric heating B7: B8: Downstream water pump B9: Solar water pump B10 : Mixing water pump B11: External circulation pump B12: B13: | 3331 | D03
Unit relay output | B0: Frequency conversion water pump B1: Auxiliary electric heating 1 B2: Auxiliary electric heating 2 B3: Chassis electric heating B4: Anti-freezing electric heating belt B5: B6: B7: | 1285 | 1541 | 1797 | 2053 | 2309 | 2565 | 2821 | 3077 | 505 | 605 | 705 | 805 | 905 | A05 | B05 | C05
Press switch input | B0: Press low pressure B1: Press high pressure B2: B3: B4: B5: B6: B7: | 1286 | 1542 | 1798 | 2054 | 2310 | 2566 | 2822 | 3078 | 506 | 606 | 706 | 806 | 906 | A06 | B06 | C06 | System switch input | B0: B1: Wire control switch B2: B3: B4: B5: B6: B7: B8: Water tank electric feedback B9: Thermostat C signal B10: Thermostat H signal B11: Solar energy signal B12: Smart grid SG signal B13: Smart grid EVU signal | 3334 | D06
Unit switch input | B0: auxiliary electric heating feedback B1: water flow switch B2: B3: B4: B5: B6: B7: | 1288 | 1544 | 1800 | 2056 | 2312 | 2568 | 2824 | 3080 | 508 | 608 | 708 | 808 | 908 | A08 | B08 | C08
Press status | B13: defrosting | 1289 | 1545 | 1801 | 2057 | 2313 | 2569 | 2825 | 3081 | 509 | 609 | 709 | 809 | 909 | A09 | B09 | C09

## 02-input, output
Read-only switching value; function code: 02
point name | illustrate | Address (decimal) | [7 empty] | Address (hexadecimal) | [7 empty] | point name | illustrate | Address (decimal) | Address (hexadecimal)
|  | 0# module | 1# module | 2# module | 3# module | 4# module | 5# module | 6# module | 7# module | 0# module | 1# module | 2# module | 3# module | 4# module | 5# module | 6# module | 7# module
Inverter compressor | Press relay output 1 | 768 | 1536 | 2304 | 3072 | 3840 | 4608 | 5376 | 6144 | 300 | 600 | 900 | C00 | F00 | 1200 | 1500 | 1800 | System relay output | defrost indication | 0 | 0
Four-way valve |  | 769 | 1537 | 2305 | 3073 | 3841 | 4609 | 5377 | 6145 | 301 | 601 | 901 | C01 | F01 | 1201 | 1501 | 1801 |  | error indication | 1 | 1
Liquid spray valve |  | 770 | 1538 | 2306 | 3074 | 3842 | 4610 | 5378 | 6146 | 302 | 602 | 902 | C02 | F02 | 1202 | 1502 | 1802 |  | external heat source | 2 | 2
spare |  | 771 | 1539 | 2307 | 3075 | 3843 | 4611 | 5379 | 6147 | 303 | 603 | 903 | C03 | F03 | 1203 | 1503 | 1803 |  | Solenoid three-way valve 1 | 3 | 3
spare |  | 772 | 1540 | 2308 | 3076 | 3844 | 4612 | 5380 | 6148 | 304 | 604 | 904 | C04 | F04 | 1204 | 1504 | 1804 |  | Solenoid three-way valve 3 | 4 | 4
Electric crankshaft heating 1 |  | 773 | 1541 | 2309 | 3077 | 3845 | 4613 | 5381 | 6149 | 305 | 605 | 905 | C05 | F05 | 1205 | 1505 | 1805 |  | Solenoid three-way valve 2 | 5 | 5
spare |  | 774 | 1542 | 2310 | 3078 | 3846 | 4614 | 5382 | 6150 | 306 | 606 | 906 | C06 | F06 | 1206 | 1506 | 1806 |  | electric water tank | 6 | 6
Electric crankshaft heating 2 |  | 775 | 1543 | 2311 | 3079 | 3847 | 4615 | 5383 | 6151 | 307 | 607 | 907 | C07 | F07 | 1207 | 1507 | 1807 |  | spare | 7 | 7
spare |  | 776 | 1544 | 2312 | 3080 | 3848 | 4616 | 5384 | 6152 | 308 | 608 | 908 | C08 | F08 | 1208 | 1508 | 1808 |  | Lower return pump | 8 | 8
spare |  | 777 | 1545 | 2313 | 3081 | 3849 | 4617 | 5385 | 6153 | 309 | 609 | 909 | C09 | F09 | 1209 | 1509 | 1809 |  | solar water pump | 9 | 9
spare |  | 778 | 1546 | 2314 | 3082 | 3850 | 4618 | 5386 | 6154 | 30A | 60A | 90A | C0A | F0A | 120A | 150A | 180A |  | Mixing pump | 10 | A
spare |  | 779 | 1547 | 2315 | 3083 | 3851 | 4619 | 5387 | 6155 | 30B | 60B | 90B | C0B | F0B | 120B | 150B | 180B |  | External circulation pump | 11 | B
spare |  | 780 | 1548 | 2316 | 3084 | 3852 | 4620 | 5388 | 6156 | 30C | 60C | 90C | C0C | F0C | 120C | 150C | 180C |  | spare | 12 | C
spare |  | 781 | 1549 | 2317 | 3085 | 3853 | 4621 | 5389 | 6157 | 30D | 60D | 90D | C0D | F0D | 120D | 150D | 180D |  | spare | 13 | D.
spare |  | 782 | 1550 | 2318 | 3086 | 3854 | 4622 | 5390 | 6158 | 30E | 60E | 90E | C0E | F0E | 120E | 150E | 180E |  | spare | 14 | E.
spare |  | 783 | 1551 | 2319 | 3087 | 3855 | 4623 | 5391 | 6159 | 30F | 60F | 90F | C0F | F0F | 120F | 150F | 180F |  | spare | 15 | f
Frequency conversion water pump | Unit relay output | 800 | 1568 | 2336 | 3104 | 3872 | 4640 | 5408 | 6176 | 320 | 620 | 920 | C20 | F20 | 1220 | 1520 | 1820
Auxiliary heater 1 |  | 801 | 1569 | 2337 | 3105 | 3873 | 4641 | 5409 | 6177 | 321 | 621 | 921 | C21 | F21 | 1221 | 1521 | 1821
Auxiliary heating 2 |  | 802 | 1570 | 2338 | 3106 | 3874 | 4642 | 5410 | 6178 | 322 | 622 | 922 | C22 | F22 | 1222 | 1522 | 1822
Electric chassis heating |  | 803 | 1571 | 2339 | 3107 | 3875 | 4643 | 5411 | 6179 | 323 | 623 | 923 | C23 | F23 | 1223 | 1523 | 1823
Anti-freezing electric heating belt |  | 804 | 1572 | 2340 | 3108 | 3876 | 4644 | 5412 | 6180 | 324 | 624 | 924 | C24 | F24 | 1224 | 1524 | 1824
spare |  | 805 | 1573 | 2341 | 3109 | 3877 | 4645 | 5413 | 6181 | 325 | 625 | 925 | C25 | F25 | 1225 | 1525 | 1825
spare |  | 806 | 1574 | 2342 | 3110 | 3878 | 4646 | 5414 | 6182 | 326 | 626 | 926 | C26 | F26 | 1226 | 1526 | 1826
spare |  | 807 | 1575 | 2343 | 3111 | 3879 | 4647 | 5415 | 6183 | 327 | 627 | 927 | C27 | F27 | 1227 | 1527 | 1827
spare |  | 808 | 1576 | 2344 | 3112 | 3880 | 4648 | 5416 | 6184 | 328 | 628 | 928 | C28 | F28 | 1228 | 1528 | 1828
spare |  | 809 | 1577 | 2345 | 3113 | 3881 | 4649 | 5417 | 6185 | 329 | 629 | 929 | C29 | F29 | 1229 | 1529 | 1829
spare |  | 810 | 1578 | 2346 | 3114 | 3882 | 4650 | 5418 | 6186 | 32A | 62A | 92A | C2A | F2A | 122A | 152A | 182A
spare |  | 811 | 1579 | 2347 | 3115 | 3883 | 4651 | 5419 | 6187 | 32B | 62B | 92B | C2B | F2B | 122B | 152B | 182B
spare |  | 812 | 1580 | 2348 | 3116 | 3884 | 4652 | 5420 | 6188 | 32C | 62C | 92C | C2C | F2C | 122C | 152C | 182C
spare |  | 813 | 1581 | 2349 | 3117 | 3885 | 4653 | 5421 | 6189 | 32D | 62D | 92D | C2D | F2D | 122D | 152D | 182D
spare |  | 814 | 1582 | 2350 | 3118 | 3886 | 4654 | 5422 | 6190 | 32E | 62E | 92E | C2E | F2E | 122E | 152E | 182E
spare |  | 815 | 1583 | 2351 | 3119 | 3887 | 4655 | 5423 | 6191 | 32F | 62F | 92F | C2F | F2F | 122F | 152F | 182F
low voltage switch | Press switch input 1 | 816 | 1584 | 2352 | 3120 | 3888 | 4656 | 5424 | 6192 | 330 | 630 | 930 | C30 | F30 | 1230 | 1530 | 1830 | System switch input | spare | 48 | 30
High voltage switch |  | 817 | 1585 | 2353 | 3121 | 3889 | 4657 | 5425 | 6193 | 331 | 631 | 931 | C31 | F31 | 1231 | 1531 | 1831 |  | remote control switch | 49 | 31
spare |  | 818 | 1586 | 2354 | 3122 | 3890 | 4658 | 5426 | 6194 | 332 | 632 | 932 | C32 | F32 | 1232 | 1532 | 1832 |  | spare | 50 | 32
spare |  | 819 | 1587 | 2355 | 3123 | 3891 | 4659 | 5427 | 6195 | 333 | 633 | 933 | C33 | F33 | 1233 | 1533 | 1833 |  | spare | 51 | 33
spare |  | 820 | 1588 | 2356 | 3124 | 3892 | 4660 | 5428 | 6196 | 334 | 634 | 934 | C34 | F34 | 1234 | 1534 | 1834 |  | spare | 52 | 34
spare |  | 821 | 1589 | 2357 | 3125 | 3893 | 4661 | 5429 | 6197 | 335 | 635 | 935 | C35 | F35 | 1235 | 1535 | 1835 |  | spare | 53 | 35
spare |  | 822 | 1590 | 2358 | 3126 | 3894 | 4662 | 5430 | 6198 | 336 | 636 | 936 | C36 | F36 | 1236 | 1536 | 1836 |  | spare | 54 | 36
spare |  | 823 | 1591 | 2359 | 3127 | 3895 | 4663 | 5431 | 6199 | 337 | 637 | 937 | C37 | F37 | 1237 | 1537 | 1837 |  | spare | 55 | 37
spare |  | 824 | 1592 | 2360 | 3128 | 3896 | 4664 | 5432 | 6200 | 338 | 638 | 938 | C38 | F38 | 1238 | 1538 | 1838 |  | Water tank heating feedback | 56 | 38
spare |  | 825 | 1593 | 2361 | 3129 | 3897 | 4665 | 5433 | 6201 | 339 | 639 | 939 | C39 | F39 | 1239 | 1539 | 1839 |  | Thermostat C signal | 57 | 39
spare |  | 826 | 1594 | 2362 | 3130 | 3898 | 4666 | 5434 | 6202 | 33A | 63A | 93A | C3A | F3A | 123A | 153A | 183A |  | Thermostat H signal | 58 | 3A
spare |  | 827 | 1595 | 2363 | 3131 | 3899 | 4667 | 5435 | 6203 | 33B | 63B | 93B | C3B | F3B | 123B | 153B | 183B |  | solar signal | 59 | 3B
spare |  | 828 | 1596 | 2364 | 3132 | 3900 | 4668 | 5436 | 6204 | 33C | 63C | 93C | C3C | F3C | 123C | 153C | 183C |  | Smart grid SG signal | 60 | 3C
spare |  | 829 | 1597 | 2365 | 3133 | 3901 | 4669 | 5437 | 6205 | 33D | 63D | 93D | C3D | F3D | 123D | 153D | 183D |  | Smart grid EVU signal | 61 | 3D
spare |  | 830 | 1598 | 2366 | 3134 | 3902 | 4670 | 5438 | 6206 | 33E | 63E | 93E | C3E | F3E | 123E | 153E | 183E |  | spare | 62 | 3E
spare |  | 831 | 1599 | 2367 | 3135 | 3903 | 4671 | 5439 | 6207 | 33F | 63F | 93F | C3F | F3F | 123F | 153F | 183F |  | spare | 63 | 3F
Auxiliary Electrothermal Feedback | Unit switch input | 848 | 1616 | 2384 | 3152 | 3920 | 4688 | 5456 | 6224 | 350 | 650 | 950 | C50 | F50 | 1250 | 1550 | 1850
Flow switch |  | 849 | 1617 | 2385 | 3153 | 3921 | 4689 | 5457 | 6225 | 351 | 651 | 951 | C51 | F51 | 1251 | 1551 | 1851
spare |  | 850 | 1618 | 2386 | 3154 | 3922 | 4690 | 5458 | 6226 | 352 | 652 | 952 | C52 | F52 | 1252 | 1552 | 1852
spare |  | 851 | 1619 | 2387 | 3155 | 3923 | 4691 | 5459 | 6227 | 353 | 653 | 953 | C53 | F53 | 1253 | 1553 | 1853
spare |  | 852 | 1620 | 2388 | 3156 | 3924 | 4692 | 5460 | 6228 | 354 | 654 | 954 | C54 | F54 | 1254 | 1554 | 1854
spare |  | 853 | 1621 | 2389 | 3157 | 3925 | 4693 | 5461 | 6229 | 355 | 655 | 955 | C55 | F55 | 1255 | 1555 | 1855
spare |  | 854 | 1622 | 2390 | 3158 | 3926 | 4694 | 5462 | 6230 | 356 | 656 | 956 | C56 | F56 | 1256 | 1556 | 1856
spare |  | 855 | 1623 | 2391 | 3159 | 3927 | 4695 | 5463 | 6231 | 357 | 657 | 957 | C57 | F57 | 1257 | 1557 | 1857
spare |  | 856 | 1624 | 2392 | 3160 | 3928 | 4696 | 5464 | 6232 | 358 | 658 | 958 | C58 | F58 | 1258 | 1558 | 1858
spare |  | 857 | 1625 | 2393 | 3161 | 3929 | 4697 | 5465 | 6233 | 359 | 659 | 959 | C59 | F59 | 1259 | 1559 | 1859
spare |  | 858 | 1626 | 2394 | 3162 | 3930 | 4698 | 5466 | 6234 | 35A | 65A | 95A | C5A | F5A | 125A | 155A | 185A
spare |  | 859 | 1627 | 2395 | 3163 | 3931 | 4699 | 5467 | 6235 | 35B | 65B | 95B | C5B | F5B | 125B | 155B | 185B
spare |  | 860 | 1628 | 2396 | 3164 | 3932 | 4700 | 5468 | 6236 | 35C | 65C | 95C | C5C | F5C | 125C | 155C | 185C
spare |  | 861 | 1629 | 2397 | 3165 | 3933 | 4701 | 5469 | 6237 | 35D | 65D | 95D | C5D | F5D | 125D | 155D | 185D
spare |  | 862 | 1630 | 2398 | 3166 | 3934 | 4702 | 5470 | 6238 | 35E | 65E | 95E | C5E | F5E | 125E | 155E | 185E
spare |  | 863 | 1631 | 2399 | 3167 | 3935 | 4703 | 5471 | 6239 | 35F | 65F | 95F | C5F | F5F | 125F | 155F | 185F

## 04-Fault
Read-only integer; function code: 04
point name | illustrate | Address (decimal) | [7 empty] | Address (hexadecimal) | [7 empty] | point name | illustrate | Address (decimal) | Address (hexadecimal)
|  | 0# module | 1# module | 2# module | 3# module | 4# module | 5# module | 6# module | 7# module | 0# module | 1# module | 2# module | 3# module | 4# module | 5# module | 6# module | 7# module
Press failure 1 | B0: Compressor low pressure B1: Compressor high pressure B2: B3: B4: Fin temperature failure B5: Exhaust temperature failure B6: Exhaust temperature too high B7: J5 pressure transmission failure B8: J6 pressure transmission failure B9: Compressor low pressure Too low B10: Compressor high pressure is too high B11: Suction temperature fault B12: B13: Suction temperature is too low B14: Frequent emergency defrosting B15: Suction and discharge temperature difference is normal | 1294 | 1550 | 1806 | 2062 | 2318 | 2574 | 2830 | 3086 | 50E | 60E | 70E | 80E | 90E | A0E | B0E | C0E | System failure 1 | B0: B1: B2: EEPROM data error B3: B4: B5: total outlet water temperature fault B6: system maintenance data error B7: B8: B9: B10: water tank electric heating overload B11: B12: hot water tank temperature fault B13: B14: system Total outlet water temperature fault B15: Floor heating water inlet temperature fault | 3342 | D0E
Press failure 2 | B0: Refrigeration evaporation is too low B1: B2: Ring temperature limit compressor is turned on B3: Plate swap return water temperature is too low B4: Plate swap return water temperature is too high B5: Fan 1 speed abnormal B6: Fan 2 speed abnormal B7: B8: B9: B10: B11: Frequency conversion communication failure B12: Frequency conversion failure B13: Frequency conversion model setting B14: B15: | 1295 | 1551 | 1807 | 2063 | 2319 | 2575 | 2831 | 3087 | 50F | 60F | 70F | 80F | 90F | A0F | B0F | C0F | System failure 2 | B0: Communication failure of wind disk 01 B1: Communication failure of wind disk 02 B2: Communication failure of wind disk 03 B3: Communication failure of wind disk 04 B4: Communication failure of wind disk 05 B5: Communication failure of wind disk 06 B6: Communication failure of wind disk 07 B7 : Communication failure of wind disk 08 B8: Communication failure of wind disk 09 B9: Communication failure of wind disk 10 B10: Communication failure of wind disk 11 B11: Communication failure of wind disk 12 B12: Communication failure of wind disk 13 B13: Communication failure of wind disk 14 B14: Wind disk 15 communication failure B15: Wind disk 16 communication failure | 3343 | D0F
Press failure 3 | B0: Refrigerant gas side temperature fault B1: Refrigerant liquid side temperature fault B2: Evaporation temperature is too high | 1296 | 1552 | 1808 | 2064 | 2320 | 2576 | 2832 | 3088 | 510 | 610 | 710 | 810 | 910 | A10 | B10 | C10 | System failure 3 | B0: Wind disk 01 failure B1: Wind disk 02 failure B2: Wind disk 03 failure B3: Wind disk 04 failure B4: Wind disk 05 failure B5: Wind disk 06 failure B6: Wind disk 07 failure B7: Wind disk 08 failure B8: Fault of wind disk 09 B9: Fault of wind disk 10 B10: Fault of wind disk 11 B11: Fault of wind disk 12 B12: Fault of wind disk 13 B13: Fault of wind disk 14 B14: Fault of wind disk 15 B15: Fault of wind disk 17 | 3344 | D10
unit failure 1 | B0: Ambient temperature fault B1: Communication fault B2: EEPROM data error B3: Auxiliary electric heating overload B4: Water tank electric heating overload B5: Board replacement water temperature is too low B6: Board replacement water temperature is too high B7: Board replacement water temperature fault B8: Water flow Insufficient B9: B10: board replacement return water temperature fault B11: total outlet water temperature fault B12: B13: board replacement return temperature difference is too large B14: board replacement return temperature difference is normal B15: frequency conversion pump warning [80%] | 1298 | 1554 | 1810 | 2066 | 2322 | 2578 | 2834 | 3090 | 512 | 612 | 712 | 812 | 912 | A12 | B12 | C12 | System failure 4 | B0: Communication failure of wind disk 17 B1: Communication failure of wind disk 18 B2: Communication failure of wind disk 19 B3: Communication failure of wind disk 20 B4: Communication failure of wind disk 21 B5: Communication failure of wind disk 22 B6: Communication failure of wind disk 23 B7 : Communication failure of wind disk 24 B8: Communication failure of wind disk 25 B9: Communication failure of wind disk 26 B10: Communication failure of wind disk 27 B11: Communication failure of wind disk 28 B12: Communication failure of wind disk 29 B13: Communication failure of wind disk 30 B14: Wind disk 31 communication failure B15: Wind disk 32 communication failure | 3345 | D11
unit failure 2 | B0: Communication abnormality B1: Internal and external machine communication failure B2: Protocol version too low B3: Frequency conversion pump failure B4: Model setting abnormality | 1299 | 1555 | 1811 | 2067 | 2323 | 2579 | 2835 | 3091 | 513 | 613 | 713 | 813 | 913 | A13 | B13 | C13 | System failure 5 | B0: Fault of wind disk 17 B1: Fault of wind disk 18 B2: Fault of wind disk 19 B3: Fault of wind disk 20 B4: Fault of wind disk 21 B5: Fault of wind disk 22 B6: Fault of wind disk 23 B7: Fault of wind disk 24 B8: Fault of wind disk 25 B9: Fault of wind disk 26 B10: Fault of wind disk 27 B11: Fault of wind disk 28 B12: Fault of wind disk 29 B13: Fault of wind disk 30 B14: Fault of wind disk 31 B15: Fault of wind disk 32 | 3346 | D12
[18 empty] | System failure 6 | B0: temperature fault at the upper part of the buffer water tank B1: temperature fault at the lower part of the buffer water tank B2: solar temperature fault B3: communication fault with the wire controllerB4: Air conditioner total outlet water temperature failure B5: Indoor temperature fault B6: Frequency conversion water pump fault | 3347 | D13

## 02-Fault
Read-only switching value; function code: 02
point name |  | illustrate | address (decimal) | [8 empty] | address (hexadecimal) | [7 empty] | point name | point name English | illustrate | address (decimal) | address (hexadecimal)
|  |  | 0#module | 1#module | 2#module | 3#module |  | 4#module | 5#module | 6#module | 7#module | 0#module | 1#module | 2#module | 3#module | 4#module | 5#module | 6#module | 7#module
low pressure | low pressure | Press failure 1 | 944 | 1712 | 2480 | 3248 | compressor error 1 | 4016 | 4784 | 5552 | 6320 | 3B0 | 6B0 | 9B0 | CB0 | FB0 | 12B0 | 15B0 | 18B0 | spare |  | System failure 1 | 176 | B0
high pressure | high pressure |  | 945 | 1713 | 2481 | 3249 |  | 4017 | 4785 | 5553 | 6321 | 3B1 | 6B1 | 9B1 | CB1 | FB1 | 12B1 | 15B1 | 18B1 | spare |  |  | 177 | B1
spare | spare |  | 946 | 1714 | 2482 | 3250 |  | 4018 | 4786 | 5554 | 6322 | 3B2 | 6B2 | 9B2 | CB2 | FB2 | 12B2 | 15B2 | 18B2 | EEPROM data error |  |  | 178 | B2
spare | spare |  | 947 | 1715 | 2483 | 3251 |  | 4019 | 4787 | 5555 | 6323 | 3B3 | 6B3 | 9B3 | CB3 | FB3 | 12B3 | 15B3 | 18B3 | spare |  |  | 179 | B3
Faulty fin temperature probe | Faulty fin temperature probe |  | 948 | 1716 | 2484 | 3252 |  | 4020 | 4788 | 5556 | 6324 | 3B4 | 6B4 | 9B4 | CB4 | FB4 | 12B4 | 15B4 | 18B4 | spare |  |  | 180 | B4
Exhaust temperature probe failure | Exhaust temperature probe failure |  | 949 | 1717 | 2485 | 3253 |  | 4021 | 4789 | 5557 | 6325 | 3B5 | 6B5 | 9B5 | CB5 | FB5 | 12B5 | 15B5 | 18B5 | Total outlet water temperature failure |  |  | 181 | B5
Exhaust temperature is too high | Exhaust temperature is too high |  | 950 | 1718 | 2486 | 3254 |  | 4022 | 4790 | 5558 | 6326 | 3B6 | 6B6 | 9B6 | CB6 | FB6 | 12B6 | 15B6 | 18B6 | System maintenance data error |  |  | 182 | B6
J5 pressure transmission failure | J5 pressure transmission failure |  | 951 | 1719 | 2487 | 3255 |  | 4023 | 4791 | 5559 | 6327 | 3B7 | 6B7 | 9B7 | CB7 | FB7 | 12B7 | 15B7 | 18B7 | spare |  |  | 183 | B7
J6 pressure transmission failure | J6 pressure transmission failure |  | 952 | 1720 | 2488 | 3256 |  | 4024 | 4792 | 5560 | 6328 | 3B8 | 6B8 | 9B8 | CB8 | FB8 | 12B8 | 15B8 | 18B8 | spare |  |  | 184 | B8
Low pressure too low | Low pressure too low |  | 953 | 1721 | 2489 | 3257 |  | 4025 | 4793 | 5561 | 6329 | 3B9 | 6B9 | 9B9 | CB9 | FB9 | 12B9 | 15B9 | 18B9 | spare |  |  | 185 | B9
High pressure is too high | High pressure is too high |  | 954 | 1722 | 2490 | 3258 |  | 4026 | 4794 | 5562 | 6330 | 3BA | 6BA | 9BA | CBA | FBA | 12BA | 15BA | 18BA | Water tank electric thermal overload |  |  | 186 | BA
Suction temperature failure | Suction temperature failure |  | 955 | 1723 | 2491 | 3259 |  | 4027 | 4795 | 5563 | 6331 | 3BB | 6BB | 9BB | CBB | FBB | 12BB | 15BB | 18BB | spare |  |  | 187 | BB
spare | spare |  | 956 | 1724 | 2492 | 3260 |  | 4028 | 4796 | 5564 | 6332 | 3BC | 6BC | 9BC | CBC | FBC | 12BC | 15BC | 18BC | Hot water tank temperature failure |  |  | 188 | BC
Suction temperature is too low | Suction temperature is too low |  | 957 | 1725 | 2493 | 3261 |  | 4029 | 4797 | 5565 | 6333 | 3BD | 6BD | 9BD | CBD | FBD | 12BD | 15BD | 18BD | spare |  |  | 189 | BD
frequent emergency defrost | frequent emergency defrost |  | 958 | 1726 | 2494 | 3262 |  | 4030 | 4798 | 5566 | 6334 | 3BE | 6BE | 9BE | CBE | FBE | 12BE | 15BE | 18BE | System total outlet water temperature failure |  |  | 190 | BE
Suction and discharge temperature difference is abnormal | Suction and discharge temperature difference is abnormal |  | 959 | 1727 | 2495 | 3263 |  | 4031 | 4799 | 5567 | 6335 | 3BF | 6BF | 9BF | CBF | FBF | 12BF | 15BF | 18BF | Underfloor heating water temperature failure |  |  | 191 | BF
Refrigeration evaporation is too low | Refrigeration evaporation is too low | Press failure 2 | 960 | 1728 | 2496 | 3264 | compressor error 2 | 4032 | 4800 | 5568 | 6336 | 3C0 | 6C0 | 9C0 | CC0 | FC0 | 12C0 | 15C0 | 18C0 | spare |  | System failure 2 | 192 | C0
spare | spare |  | 961 | 1729 | 2497 | 3265 |  | 4033 | 4801 | 5569 | 6337 | 3C1 | 6C1 | 9C1 | CC1 | FC1 | 12C1 | 15C1 | 18C1 | spare |  |  | 193 | C1
Ambient temperature limit compressor on | Ambient temperature limit compressor on |  | 962 | 1730 | 2498 | 3266 |  | 4034 | 4802 | 5570 | 6338 | 3C2 | 6C2 | 9C2 | CC2 | FC2 | 12C2 | 15C2 | 18C2 | spare |  |  | 194 | C2
Plate replacement return water temperature is too low | Plate replacement return water temperature is too low |  | 963 | 1731 | 2499 | 3267 |  | 4035 | 4803 | 5571 | 6339 | 3C3 | 6C3 | 9C3 | CC3 | FC3 | 12C3 | 15C3 | 18C3 | spare |  |  | 195 | C3
Plate replacement return water temperature is too high | Plate replacement return water temperature is too high |  | 964 | 1732 | 2500 | 3268 |  | 4036 | 4804 | 5572 | 6340 | 3C4 | 6C4 | 9C4 | CC4 | FC4 | 12C4 | 15C4 | 18C4 | spare |  |  | 196 | C4
Abnormal speed of fan 1 | Abnormal speed of fan 1 |  | 965 | 1733 | 2501 | 3269 |  | 4037 | 4805 | 5573 | 6341 | 3C5 | 6C5 | 9C5 | CC5 | FC5 | 12C5 | 15C5 | 18C5 | spare |  |  | 197 | C5
Abnormal speed of fan 2 | Abnormal speed of fan 2 |  | 966 | 1734 | 2502 | 3270 |  | 4038 | 4806 | 5574 | 6342 | 3C6 | 6C6 | 9C6 | CC6 | FC6 | 12C6 | 15C6 | 18C6 | spare |  |  | 198 | C6
spare | spare |  | 967 | 1735 | 2503 | 3271 |  | 4039 | 4807 | 5575 | 6343 | 3C7 | 6C7 | 9C7 | CC7 | FC7 | 12C7 | 15C7 | 18C7 | spare |  |  | 199 | C7
spare | spare |  | 968 | 1736 | 2504 | 3272 |  | 4040 | 4808 | 5576 | 6344 | 3C8 | 6C8 | 9C8 | CC8 | FC8 | 12C8 | 15C8 | 18C8 | spare |  |  | 200 | C8
spare | spare |  | 969 | 1737 | 2505 | 3273 |  | 4041 | 4809 | 5577 | 6345 | 3C9 | 6C9 | 9C9 | CC9 | FC9 | 12C9 | 15C9 | 18C9 | spare |  |  | 201 | C9
spare | spare |  | 970 | 1738 | 2506 | 3274 |  | 4042 | 4810 | 5578 | 6346 | 3CA | 6CA | 9CA | CCA | FCA | 12CA | 15CA | 18CA | spare |  |  | 202 | CA
Frequency conversion communication failure | Frequency conversion communication failure |  | 971 | 1739 | 2507 | 3275 |  | 4043 | 4811 | 5579 | 6347 | 3CB | 6CB | 9CB | CCB | FCB | 12CB | 15CB | 18CB | spare |  |  | 203 | CB
Frequency conversion failure | Frequency conversion failure |  | 972 | 1740 | 2508 | 3276 |  | 4044 | 4812 | 5580 | 6348 | 3cc | 6cc | 9cc | CCC | FCC | 12CC | 15CC | 18CC | spare |  |  | 204 | CC
Inverter model setting | Inverter model setting |  | 973 | 1741 | 2509 | 3277 |  | 4045 | 4813 | 5581 | 6349 | 3CD | 6CD | 9CD | CCD | FCD | 12 CDs | 15 CDs | 18 CDs | spare |  |  | 205 | cd
spare | spare |  | 974 | 1742 | 2510 | 3278 |  | 4046 | 4814 | 5582 | 6350 | 3CE | 6CE | 9CE | CCE | FCE | 12CE | 15CE | 18CE | spare |  |  | 206 | CE
spare | spare |  | 975 | 1743 | 2511 | 3279 |  | 4047 | 4815 | 5583 | 6351 | 3CF | 6CF | 9CF | CCF | FCF | 12CF | 15CF | 18CF | spare |  |  | 207 | CF
Refrigerant gas side temperature failure | Refrigerant gas side temperature failure | Press failure 3 | 976 | 1744 | 2512 | 3280 | compressor error 3 | 4048 | 4816 | 5584 | 6352 | 3D0 | 6D0 | 9D0 | CD0 | FD0 | 12D0 | 15D0 | 18D0 | spare |  | System failure 3 | 208 | D0
Refrigerant liquid side temperature failure | Refrigerant liquid side temperature failure |  | 977 | 1745 | 2513 | 3281 |  | 4049 | 4817 | 5585 | 6353 | 3D1 | 6D1 | 9D1 | CD1 | FD1 | 12D1 | 15D1 | 18D1 | spare |  |  | 209 | D1
Evaporation temperature is too high | Evaporation temperature is too high |  | 978 | 1746 | 2514 | 3282 |  | 4050 | 4818 | 5586 | 6354 | 3D2 | 6D2 | 9D2 | CD2 | FD2 | 12D2 | 15D2 | 18D2 | spare |  |  | 210 | D2
spare | spare |  | 979 | 1747 | 2515 | 3283 |  | 4051 | 4819 | 5587 | 6355 | 3D3 | 6D3 | 9D3 | CD3 | FD3 | 12D3 | 15D3 | 18D3 | spare |  |  | 211 | D3
spare | spare |  | 980 | 1748 | 2516 | 3284 |  | 4052 | 4820 | 5588 | 6356 | 3D4 | 6D4 | 9D4 | CD4 | FD4 | 12D4 | 15D4 | 18D4 | spare |  |  | 212 | D4
spare | spare |  | 981 | 1749 | 2517 | 3285 |  | 4053 | 4821 | 5589 | 6357 | 3D5 | 6D5 | 9D5 | CD5 | FD5 | 12D5 | 15D5 | 18D5 | spare |  |  | 213 | D5
spare | spare |  | 982 | 1750 | 2518 | 3286 |  | 4054 | 4822 | 5590 | 6358 | 3D6 | 6D6 | 9D6 | CD6 | FD6 | 12D6 | 15D6 | 18D6 | spare |  |  | 214 | D6
spare | spare |  | 983 | 1751 | 2519 | 3287 |  | 4055 | 4823 | 5591 | 6359 | 3D7 | 6D7 | 9D7 | CD7 | FD7 | 12D7 | 15D7 | 18D7 | spare |  |  | 215 | D7
spare | spare |  | 984 | 1752 | 2520 | 3288 |  | 4056 | 4824 | 5592 | 6360 | 3D8 | 6D8 | 9D8 | CD8 | FD8 | 12D8 | 15D8 | 18D8 | spare |  |  | 216 | D8
spare | spare |  | 985 | 1753 | 2521 | 3289 |  | 4057 | 4825 | 5593 | 6361 | 3D9 | 6D9 | 9D9 | CD9 | FD9 | 12D9 | 15D9 | 18D9 | spare |  |  | 217 | D9
spare | spare |  | 986 | 1754 | 2522 | 3290 |  | 4058 | 4826 | 5594 | 6362 | 3DA | 6DA | 9DA | CDA | FDA | 12DA | 15DA | 18DA | spare |  |  | 218 | DA
spare | spare |  | 987 | 1755 | 2523 | 3291 |  | 4059 | 4827 | 5595 | 6363 | 3DB | 6DB | 9DB | CDB | FDB | 12DB | 15DB | 18DB | spare |  |  | 219 | DB
spare | spare |  | 988 | 1756 | 2524 | 3292 |  | 4060 | 4828 | 5596 | 6364 | 3DC | 6DC | 9DC | CDC | FDC | 12DC | 15DC | 18DC | spare |  |  | 220 | DC
spare | spare |  | 989 | 1757 | 2525 | 3293 |  | 4061 | 4829 | 5597 | 6365 | 3DD | 6DD | 9DD | CDD | FDD | 12DD | 15DD | 18DD | spare |  |  | 221 | DD
spare | spare |  | 990 | 1758 | 2526 | 3294 |  | 4062 | 4830 | 5598 | 6366 | 3DE | 6DE | 9DE | CDEs | FDEs | 12DE | 15DE | 18DE | spare |  |  | 222 | DE
spare | spare |  | 991 | 1759 | 2527 | 3295 |  | 4063 | 4831 | 5599 | 6367 | 3DF | 6DF | 9DF | CDF | FDF | 12DF | 15DF | 18DF | spare |  |  | 223 | DF
module ambient temperature failure | module ambient temperature failure | unit failure 1 | 1008 | 1776 | 2544 | 3312 | Unit error 1 | 4080 | 4848 | 5616 | 6384 | 3F0 | 6F0 | 9F0 | CF0 | FF0 | 12F0 | 15F0 | 18F0 | spare |  | System failure 4 | 224 | E0
communication fail | communication fail |  | 1009 | 1777 | 2545 | 3313 |  | 4081 | 4849 | 5617 | 6385 | 3F1 | 6F1 | 9F1 | CF1 | FF1 | 12F1 | 15F1 | 18F1 | spare |  |  | 225 | E1
EEPROM data error | EEPROM data error |  | 1010 | 1778 | 2546 | 3314 |  | 4082 | 4850 | 5618 | 6386 | 3F2 | 6F2 | 9F2 | CF2 | FF2 | 12F2 | 15F2 | 18F2 | spare |  |  | 226 | E2
Auxiliary electric thermal overload | Auxiliary electric thermal overload |  | 1011 | 1779 | 2547 | 3315 |  | 4083 | 4851 | 5619 | 6387 | 3F3 | 6F3 | 9F3 | CF3 | FF3 | 12F3 | 15F3 | 18F3 | spare |  |  | 227 | E3
Water tank electric thermal overload | Water tank electric thermal overload |  | 1012 | 1780 | 2548 | 3316 |  | 4084 | 4852 | 5620 | 6388 | 3F4 | 6F4 | 9F4 | CF4 | FF4 | 12F4 | 15F4 | 18F4 | spare |  |  | 228 | E4
The temperature of the water out of the plate is too low | The temperature of the water out of the plate is too low |  | 1013 | 1781 | 2549 | 3317 |  | 4085 | 4853 | 5621 | 6389 | 3F5 | 6F5 | 9F5 | CF5 | FF5 | 12F5 | 15F5 | 18F5 | spare |  |  | 229 | E5
Plate replacement water temperature is too high | Plate replacement water temperature is too high |  | 1014 | 1782 | 2550 | 3318 |  | 4086 | 4854 | 5622 | 6390 | 3F6 | 6F6 | 9F6 | CF6 | FF6 | 12F6 | 15F6 | 18F6 | spare |  |  | 230 | E6
Board replacement water temperature failure | Board replacement water temperature failure |  | 1015 | 1783 | 2551 | 3319 |  | 4087 | 4855 | 5623 | 6391 | 3F7 | 6F7 | 9F7 | CF7 | FF7 | 12F7 | 15F7 | 18F7 | spare |  |  | 231 | E7
Insufficient water flow | Insufficient water flow |  | 1016 | 1784 | 2552 | 3320 |  | 4088 | 4856 | 5624 | 6392 | 3F8 | 6F8 | 9F8 | CF8 | FF8 | 12F8 | 15F8 | 18F8 | spare |  |  | 232 | E8
spare | spare |  | 1017 | 1785 | 2553 | 3321 |  | 4089 | 4857 | 5625 | 6393 | 3F9 | 6F9 | 9F9 | CF9 | FF9 | 12F9 | 15F9 | 18F9 | spare |  |  | 233 | E9
Board replacement return water temperature failure | Board replacement return water temperature failure |  | 1018 | 1786 | 2554 | 3322 |  | 4090 | 4858 | 5626 | 6394 | 3FA | 6FA | 9FA | CFA | FFA | 12FA | 15FA | 18FA | spare |  |  | 234 | EA
Total outlet water temperature failure | Total outlet water temperature failure |  | 1019 | 1787 | 2555 | 3323 |  | 4091 | 4859 | 5627 | 6395 | 3FB | 6FB | 9FB | CFB | FFB | 12FB | 15FB | 18FB | spare |  |  | 235 | EB
spare | spare |  | 1020 | 1788 | 2556 | 3324 |  | 4092 | 4860 | 5628 | 6396 | 3FC | 6FC | 9FC | CFCs | FFC | 12FC | 15FC | 18FC | spare |  |  | 236 | EC
The temperature difference between board replacement and return is too large | The temperature difference between board replacement and return is too large |  | 1021 | 1789 | 2557 | 3325 |  | 4093 | 4861 | 5629 | 6397 | 3FD | 6FD | 9FD | CFD | FFD | 12FD | 15FD | 18FD | spare |  |  | 237 | ED
The temperature difference between board replacement and recovery is abnormal | The temperature difference between board replacement and recovery is abnormal |  | 1022 | 1790 | 2558 | 3326 |  | 4094 | 4862 | 5630 | 6398 | 3FE | 6FE | 9FE | CFE | FFE | 12FE | 15FE | 18FE | spare |  |  | 238 | EE
Frequency conversion water pump warning [80%] | Frequency conversion water pump warning [80%] |  | 1023 | 1791 | 2559 | 3327 |  | 4095 | 4863 | 5631 | 6399 | 3FF | 6FF | 9FF | CFF | FFF | 12FF | 15FF | 18FF | spare |  |  | 239 | EF
abnormal communication | abnormal communication | unit failure 2 | 1024 | 1792 | 2560 | 3328 | Unit error 2 | 4096 | 4864 | 5632 | 6400 | 400 | 700 | A00 | D00 | 1000 | 1300 | 1600 | 1900 | spare |  | System failure 5 | 240 | F0
Communication failure between internal and external units | Communication failure between internal and external units |  | 1025 | 1793 | 2561 | 3329 |  | 4097 | 4865 | 5633 | 6401 | 401 | 701 | A01 | D01 | 1001 | 1301 | 1601 | 1901 | spare |  |  | 241 | F1
The protocol version is too low | The protocol version is too low |  | 1026 | 1794 | 2562 | 3330 |  | 4098 | 4866 | 5634 | 6402 | 402 | 702 | A02 | D02 | 1002 | 1302 | 1602 | 1902 | spare |  |  | 242 | F2
Frequency conversion water pump failure | Frequency conversion water pump failure |  | 1027 | 1795 | 2563 | 3331 |  | 4099 | 4867 | 5635 | 6403 | 403 | 703 | A03 | D03 | 1003 | 1303 | 1603 | 1903 | spare |  |  | 243 | F3
The model setting is abnormal | The model setting is abnormal |  | 1028 | 1796 | 2564 | 3332 |  | 4100 | 4868 | 5636 | 6404 | 404 | 704 | A04 | D04 | 1004 | 1304 | 1604 | 1904 | spare |  |  | 244 | F4
spare | spare |  | 1029 | 1797 | 2565 | 3333 |  | 4101 | 4869 | 5637 | 6405 | 405 | 705 | A05 | D05 | 1005 | 1305 | 1605 | 1905 | spare |  |  | 245 | F5
spare | spare |  | 1030 | 1798 | 2566 | 3334 |  | 4102 | 4870 | 5638 | 6406 | 406 | 706 | A06 | D06 | 1006 | 1306 | 1606 | 1906 | spare |  |  | 246 | F6
spare | spare |  | 1031 | 1799 | 2567 | 3335 |  | 4103 | 4871 | 5639 | 6407 | 407 | 707 | A07 | D07 | 1007 | 1307 | 1607 | 1907 | spare |  |  | 247 | F7
spare | spare |  | 1032 | 1800 | 2568 | 3336 |  | 4104 | 4872 | 5640 | 6408 | 408 | 708 | A08 | D08 | 1008 | 1308 | 1608 | 1908 | spare |  |  | 248 | F8
spare | spare |  | 1033 | 1801 | 2569 | 3337 |  | 4105 | 4873 | 5641 | 6409 | 409 | 709 | A09 | D09 | 1009 | 1309 | 1609 | 1909 | spare |  |  | 249 | F9
spare | spare |  | 1034 | 1802 | 2570 | 3338 |  | 4106 | 4874 | 5642 | 6410 | 40A | 70A | A0A | D0A | 100A | 130A | 160A | 190A | spare |  |  | 250 | FA
spare | spare |  | 1035 | 1803 | 2571 | 3339 |  | 4107 | 4875 | 5643 | 6411 | 40B | 70B | A0B | D0B | 100B | 130B | 160B | 190B | spare |  |  | 251 | Facebook
spare | spare |  | 1036 | 1804 | 2572 | 3340 |  | 4108 | 4876 | 5644 | 6412 | 40C | 70C | A0C | D0C | 100C | 130C | 160C | 190C | spare |  |  | 252 | FC
spare | spare |  | 1037 | 1805 | 2573 | 3341 |  | 4109 | 4877 | 5645 | 6413 | 40D | 70D | A0D | D0D | 100D | 130D | 160D | 190D | spare |  |  | 253 | FD
spare | spare |  | 1038 | 1806 | 2574 | 3342 |  | 4110 | 4878 | 5646 | 6414 | 40E | 70E | A0E | D0E | 100E | 130E | 160E | 190E | spare |  |  | 254 | FE
spare | spare |  | 1039 | 1807 | 2575 | 3343 |  | 4111 | 4879 | 5647 | 6415 | 40F | 70F | A0F | D0F | 100F | 130F | 160F | 190F | spare |  |  | 255 | FF
[20 empty] | Buffer water tank upper temperature failure |  | System failure 6 | 256 | 100
[20 empty] | Temperature fault in the lower part of the buffer water tank |  |  | 257 | 101
[20 empty] | Solar temperature failure |  |  | 258 | 102
[20 empty] | Wire controller communication failure |  |  | 259 | 103
[20 empty] | Total outlet water temperature fault of air conditioner |  |  | 260 | 104
[20 empty] | room temperature failure |  |  | 261 | 105
[20 empty] | Frequency conversion water pump failure |  |  | 262 | 106
[20 empty] | spare |  |  | 263 | 107
[20 empty] | spare |  |  | 264 | 108
[20 empty] | spare |  |  | 265 | 109
[20 empty] | spare |  |  | 266 | 10A
[20 empty] | spare |  |  | 267 | 10B
[20 empty] | spare |  |  | 268 | 10C
[20 empty] | spare |  |  | 269 | 10D
[20 empty] | spare |  |  | 270 | 10E
[20 empty] | spare |  |  | 271 | 10F